## Parameters to fill
Parameters of cable | Values | Trefoil Formation
Total length of cable(s) (m) | 2000 | Result if Crossbondng is done / year
Frequency of the grid (Hz) | 50 | Calculated parameters | Values | Trefoil | Flat (disposition) | Flat (no disposition)
Distance between cables (m)* see disposition | 0.093 | Total cost of energy loss @ 100% capacity factor/ yr | 19201.4986
Diameter of insulation (m) | 0.075 | Total cost of energy loss per year @ capacity factor/ yr | 6451.7035
Area of cross section (conductor) | 0.001146 | Energy cost from conductor | 2784.1916
Area of cross section (sheath) | 0.00023876 | Savings if Cross bonding is done/year | 3667.512
Type of conductor (Cu/Al) * choose below | Copper
Type of sheath (Cu/Al) * choose below | Copper | Flat formation ( transposition)
Cost price of energy (Euros/kWh) | 0.1 | Result if Crossbonding is done / year
Operational hours (hrs)/year | 8760 | Calculated parameters | Values
Current in cable (A) | 275 | Total cost of energy loss @ 100% capacity factor/ yr | 22177.439
Capacity Factor (see below) | 0.336 | Total cost of energy loss per year @ capacity factor/ yr | 7451.6195
*Choose Conductor Type | Copper | Savings if Cross bonding is done/year | 4667.4279
*Choose Sheeth Type | Copper
Flat formation ( no transposition)
Result if Crossbonding is done / year
Results in Worksheets (Trefoil, Flat and Flat) |  | Calculated parameters | Values
|  | Total cost of energy loss @ 100% capacity factor/ yr | 21136.9419
* Cable parameters needs to be inserted in SI units |  | Total cost of energy loss per year @ capacity factor/ yr | 7102.0125
*Current in cable = ampacity |  | Savings if Cross bonding is done/year | 4317.8209
*Cable dimensions (in orange) can be entered from a cable data sheet
*Calculations are done as per the formula mentioned in IEC 60287-1-1
* Capacity factor is calculated for a wind farm = (Total energy produced in a year)/(Installed capacity of a wind farm *8760) [Source: https://www.cbs.nl/en-gb/figures/detail/82610ENG]
* Average Lifespan of a Windpark or Solarpark is set to 20 years
|  | Formation Type | Total Savings*
|  | Trefoil Formation | 73350.2392
|  | Flat Formation (transposition) | 93348.5584
|  | Flat Formation (no transposition) | 86356.4178
* over lifespan of park (20 years)
𝑚^2
𝑚^2
𝑚^2
𝑚^2
𝑚^2
𝑚^2
𝑚^2
𝑚^2
0.093m

## Trefoil formation
Parameters of cable | Values
Length (m) | 2000
Frequency of the grid (Hz) | 50
Distance between cables (m) | 0.093
Diameter of insulation (m) | 0.075
Area of cross section (conductor) | 0.001146
Area of cross section (sheath) | 0.00023876
Type of conductor (Cu/Al) | Copper
Type of sheath (Cu/Al) | Copper
Cost price of energy (Euros/kWh) | 0.1
Operational hours (hrs)/year | 8760
Current in cable (A) | 275
Capacity Factor | 0.336
|  | Calculated parameters | Values
|  | Conductor resistivity | 1.7241e-08 |  | Parameters | Values
|  | Sheath resitivity | 1.7241e-08 |  | xs^2 | 8.3526
|  | Resistance of conductor | 2.0847e-05 |  | DC resistance | 1.5045e-05
|  | Resistance of sheath | 7.2212e-05 |  | xp^2 | 8.3526
|  | Insulation thickness | 0.018401 |  | dc/S | 0.41074
|  | Conductor radius | 0.019099 |  | ys | 0.28153
|  | Sheath radius (rsh) | 0.0378 |  | Term1(proximity) | 0.047495
|  | Power loss in conductor | 3153.0763 |  | Term2 proximity | 2.1921
|  | Mutual inductance | 1.8006e-07 |  | yp | 0.10412
|  | Omega | 314.1593 |  | AC resistance of conductor | 2.0847e-05
|  | Mutual reactance | 5.6567e-05
|  | Sheath loss factor | 1.3173
|  | Power loss in cable in kW | 7.3065
|  | Power loss in 3 cables in kW | 21.9195 | COMSOL | 0.627
|  | Total cost of energy loss @ 100% capacity factor/ yr | 19201.4986
|  | Total cost of energy loss per year @ capacity factor/ yr | 6451.7035
|  | Energy cost from conductor | 2784.1916
|  | Savings if Cross bonding is done/year/Joint | 3667.512
*Calculations are done as per the formula mentioned in IEC 60287-1-1
* Capacity factor is calculated for a wind farm = (Total energy produced in a year)/(Installed capacity of a wind farm *8760) [Source: https://www.cbs.nl/en-gb/figures/detail/82610ENG]
* Cable parameters needs to be inserted in SI units
* Length = Length of the cable system as shown in figure [Source: https://elek.com]
*Current in cable = ampacity
*Cable dimensions (in orange) can be entered from a cable data sheet
𝑚^2
𝑚^2
0.093m
𝑚^2
𝑚^2
Length (m)

## Flat (transposition)
Parameters of cable | Values
Length (m) | 2000
Frequency of the grid (Hz) | 50
Distance between cables (m) [d as shown in figure] | 0.093
Diameter of insulation (m) | 0.075
Area of cross section (conductor) | 0.001146
Area of cross section (sheath) | 0.00023876
Type of conductor (Cu/Al) | Copper
Type of sheath (Cu/Al) | Copper
Cost price of energy (Euros/kWh) | 0.1
Operational hours (hrs) | 8760
Current in cable (A) | 275
Capacity Factor | 0.336
|  | Calculated parameters | Values | Parameters | Values
|  | Conductor resistivity | 1.7241e-08 | xs | 8.3526
|  | Sheath resitivity | 1.7241e-08 | DC resistance | 1.5045e-05
|  |  |  | xp | 8.3526
|  | Resistance of conductor | 2.0847e-05 | dc/S | 0.41074
|  | Resistance of sheath | 7.2212e-05 | ys | 0.28153
|  | Insulation thickness | 0.018401 | Term1(proximity) | 0.047495
|  | Conductor radius | 0.019099 | Term2 proximity | 2.1921
|  | Sheath radius (rsh) | 0.0385 | yp | 0.10412
|  | Power loss in conductor | 3153.0763 | AC resistance of conductor | 2.0847e-05
|  | Mutual inductance | 2.226e-07
|  | Omega | 314.1593
|  | Mutual reactance | 6.9931e-05
|  | Sheath loss factor | 1.6764
|  | Power loss in cable in kW | 8.4389
|  | Power loss in 3 cables in KW | 25.3167
|  | Total cost of energy loss @ 100% capacity factor/ yr | 22177.439
|  | Total cost of energy loss per year @ capacity factor/ yr | 7451.6195
|  | Energy cost from conductor | 2784.1916
|  | Savings if Cross bonding is done/year/joint | 4667.4279
*Calculations are done as per the formula mentioned in IEC 60287-1-1
* Capacity factor is calculated for a wind farm = (Total energy produced in a year)/(Installed capacity of a wind farm *8760) [Source: https://www.cbs.nl/en-gb/figures/detail/82610ENG]
* Cable parameters needs to be inserted in SI units
* Length of the cable system = distance between the grounding points as shown in figure
*Current in cable = ampacity
*Cable dimensions (in orange) can be entered from a cable data sheet
𝑚^2
𝑚^2
𝑚^2
𝑚^2
Transposition scheme

## Flat (no transposition)
Parameters of cable | Values
Length (m) | 2000
Frequency of the grid (Hz) | 50
Distance between cables (m) [d as shown in figure] | 0.093
Diameter of insulation (m) | 0.075
Area of cross section (conductor) | 0.001146
Area of cross section (sheath) | 0.00023876
Type of conductor (Cu/Al) | Copper
Type of sheath (Cu/Al) | Copper
Cost price of energy (Euro/kWh) | 0.1
Operational hours (hrs) | 8760
Current in cable (A) | 275
Capacity Factor | 0.336
|  | Calculated parameters | Values | Parameters | Values
|  | Conductor resistivity | 1.7241e-08 | xs | 8.3526
* Cable parameters needs to be inserted in SI units * Operation of the cable is considered for 24*7 * Cables are equidistant from each other |  | Sheath resitivity | 1.7241e-08 | DC resistance | 1.5045e-05
|  | Resistance of conductor | 2.0847e-05 | xp | 2.8901
|  | Resistance of sheath | 7.2212e-05 | dc/S | 0.41074
|  | Insulation thickness | 0.018401 | ys | 0.28153
|  | Conductor radius | 0.019099 | Term1(proximity) | 0.047495
|  | Sheath radius (rsh) | 0.0385 | Term2 proximity | 2.1921
|  | Power loss in conductor | 3153.0763 | yp | 0.10412
|  | X | 5.5414e-05 | AC resistance of conductor | 2.0847e-05
|  | Omega | 314.1593
|  | Xm | 4.3552e-05
|  | P | 9.8966e-05
|  | Q | 4.0897e-05
|  | Term1 | 0.48942
|  | Term2 | 0.060713
|  | Term 3 | 0.14219
|  | Sheath loss factor outer cable | 2.3982
|  | Sheath loss factor outer cable 2 | 1.4131
|  | Sheath loss factor middle cable | 0.84122
|  | Power loss in outer cable | 10714.7372
|  | Power loss in outer cable 2 | 7608.6819
|  | Power loss in middle cable | 5805.51
|  | Total power loss in 3 cables in kW | 24.1289
|  | Total cost of energy loss @ 100% capacity factor/ yr | 21136.9419
|  | Total cost of energy loss per year @ capacity factor/ yr | 7102.0125
|  | Energy cost from conductor | 2784.1916
|  | Savings if Cross bonding is done/year/joint | 4317.8209
*Calculations are done as per the formula mentioned in IEC 60287-1-1
* Capacity factor is calculated for a wind farm = (Total energy produced in a year)/(Installed capacity of a wind farm *8760) [Source: https://www.cbs.nl/en-gb/figures/detail/82610ENG]
* Cable parameters needs to be inserted in SI units
* Length of the cable system = distance between the grounding points as shown in figure
*For flat formation 'd' as shown in figure is the distance between the cables
*Current in cable = ampacity
*Cable dimensions (in orange) can be entered from a cable data sheet
𝑚^2
𝑚^2
No Transposition